## FLEXIBLE WIRING SURFIX CABLE

### 300/500V

##### Cable Description

Copper conductors to SANS 1411 Part 1, PVC insulated to SANS 1411 Part 2, laid up with a bare tinned copper earth wire in contact with a longitudinal aluminium/polyethylene laminate, uV stable PVC sheathed to SANS 1411 Part 2.

##### Installation Information

Complies with SANS 10142 “Code of Practice for Wiring of Premises” Section 6:

  Surface wiring

  Under-plastering wiring

  Wiring in hollow walls

  Wiring in roof spaces

##### Properties

  UV Stable

  Sheath Identification : White or Black

  Specifications : SANS 1507-2

  Temperature Range :-10°C to 70°C

  Voltage Rating : 300/500V

Core Identification : 2 Core - Red and black, 3 Core - Red, yellow, blue, 4 Core - Red, yellow, blue, black

Packaging

  100mt shrink-wrapped coils

  Available on 500 and 1000mt wooden drums on request (depending on size)

### Technical Data

| Cable Size* |  | Electrical Properties |  |  |  |  | Physical Properties |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Conductor Resistance (DC @ 20ºC) |  | Current Rating** | Voltage Drop*** | 1 Second Short Circuit Rating | Approximate Overall Diameter | Approximate Cable Mass |
| Phase (mm2) | Earth (mm2) | Phase (Ω/km) | Earth (Ω/km) |  |  |  |  |  |
|  |  |  |  | (A) | (mV/A/mt) | (kA) | (mm) | (kg/100mt) |
| 2 Core |  |  |  |  |  |  |  |  |
| 1.5 | 1 | 12.1 | 18.2 | 17 | 29 | 0.14 | 7.8 | 10.6 |
| 2.5 | 1.5 | 7.41 | 12.2 | 23 | 18 | 0.24 | 8.8 | 14.4 |
| 4 |  | 4.61 |  | 30 | 11 | 0.38 | 10.1 | 20.8 |
| 6 | 2.5 | 3.08 | 7.56 | 38 | 7.3 | 0.58 | 11.3 | 25.7 |
| 3 Core |  |  |  |  |  |  |  |  |
| 1.5 | 1 | 12.1 | 18.2 | 15 | 25 | 0.14 | 8.0 | 10.9 |
| 2.5 | 1.5 | 7.41 | 12.2 | 20 | 15 | 0.24 | 9.3 | 15.7 |
| 4 |  | 4.61 |  | 27 | 9.5 | 0.38 | 10.8 | 21.0 |
| 6 | 2.5 | 3.08 | 7.56 | 34 | 6.4 | 0.58 | 12.0 | 28.7 |
| 4 Core |  |  |  |  |  |  |  |  |
| 1.5 | 1 | 12.1 | 18.2 | 15 | 25 | 0.14 | 8.7 | 13.3 |
| 2.5 | 1.5 | 7.41 | 12.2 | 20 | 15 | 0.24 | 10.2 | 19.3 |
| 4 |  | 4.61 |  | 27 | 9.5 | 0.38 | 11.8 | 26.5 |
| 6 | 2.5 | 3.08 | 7.56 | 34 | 6.4 | 0.58 | 12.8 | 33.5 |

### Product Code

| Cable Size | Black |  |  | White |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| (mm2) | 2 Core | 3 Core | 4 Core | 2 Core | 3 Core | 4 Core |
| 1.5 | F0000598 | F0000603 | F0000608 | F0000600 | F0000605 | F0000609 |
| 2.5 | F0000614 | F0000619 | F0000623 | F0000616 | F0000620 | F0000624 |
| 4 | F0000627 | F0000631 | F0000635 | F0000628 | F0000632 | F0000636 |
| 6 | F0000639 | F0000641 | F0000643 | F0000640 | F0000642 | F0000644 |
| 10 | F0000610 |  |  | F0000611 |  |  |